## Regression
VOCO Bangkok Sukhumvit 11 – column skill v1.2 regression vs issued design (S-04-01-01 R3 / Excel calc files 03_xx)
Same loads, section, f'c, Lu, k, βd as each Excel file (load sheet = envelope of all ETABS labels in that file). Shear not compared (no V in load sheets). Rev.1 (19 Oct 2026): less steel allowed below the f'c change; C1 B6-B5 Lu 2.75 m, k 1.0 (designer).
Mark | Band (Excel file) | Section b×h (mm) | f'c (ksc) | Lu (m) | k | Excel "Using" | Drawing S-04-01-01 R3 | As drawing (cm²) | D/C drawing bars (engine) | Engine v1.2 bars | As engine (cm²) | D/C engine | ρ engine | Status | δ max | ΔAs engine vs drawing | Flag
C1 | B6-B5 | 450x2000 | 560 | 2.75 | 1 | 66-DB32 | 66-32 | 530.8 | 0.976 | 62-DB32 | 498.63 | 0.998 | 5.54% | OK | 1 | -6.061%
C1 | B4-B3 | 450x2000 | 560 | 4.5 | 0.9 | 42-DB32 | 44-32 (eval 46) | 353.87 | 0.942 | 42-DB32 | 337.78 | 0.967 | 3.75% | OK | 1.93 | -4.547%
C1 | B2-B1 | 450x2000 | 560 | 4.5 | 0.9 | 22-DB32 | 22-32 | 176.93 | 1.142 | 30-DB32 | 241.27 | 0.998 | 2.68% | OK | 2.07 | 36.36% | drawing bars D/C>1 – review
C1 | 1st - 3th | 450x2000 | 560 | 4.5 | 0.9 | 22-DB28 | 22-28 | 135.47 | 0.977 | 30-DB25 | 147.26 | 0.942 | 1.64% | OK | 2.18 | 8.703%
C1 | 4th-10th | 450x2000 | 400 | 4.5 | 0.9 | 42-DB28 | 44-28 (eval 46) | 270.93 | 0.858 | 30-DB28 | 184.73 | 0.969 | 2.05% | OK | 1.86 | -31.82% | ΔAs > 30 %
C1 | 11th-20th | 450x2000 | 400 | 4.5 | 0.9 | 22-DB25 | 22-25 | 107.99 | 0.782 | 30-DB20 | 94.25 | 0.823 | 1.05% | OK | 1.59 | -12.72%
C2 | B6-B1 | 450x2000 | 560 | 4.5 | 0.9 | 42-DB28 | 44-28 (eval 46) | 270.93 | 0.846 | 30-DB28 | 184.73 | 0.957 | 2.05% | OK | 2.11 | -31.82% | ΔAs > 30 %
C2 | 1st-3th | 450x2000 | 560 | 4.5 | 0.9 | 22-DB28 | 22-28 | 135.47 | 0.554 | 30-DB20 | 94.25 | 0.582 | 1.05% | OK | 1.65 | -30.43% | ΔAs > 30 %
C2 | 4th-14th | 450x2000 | 400 | 4.5 | 0.9 | 22-DB25 | 22-25 | 107.99 | 0.541 | 30-DB20 | 94.25 | 0.549 | 1.05% | OK | 1.46 | -12.72%
C2s | 15th-20th | 450x1200 | 400 | 4.5 | 0.9 | 24-DB25 | 24-25 (eval 26) | 117.81 | 0.756 | 20-DB25 | 98.17 | 0.91 | 1.82% | OK | 1.22 | -16.67%
C3 | B6-B1 | 450x2000 | 560 | 4.5 | 0.9 | 42-DB28 | 44-28 (eval 46) | 270.93 | 0.846 | 30-DB28 | 184.73 | 0.957 | 2.05% | OK | 2.11 | -31.82% | ΔAs > 30 %
C3 | 1st-3th | 450x2000 | 560 | 4.5 | 0.9 | 42-DB28 | 44-28 (eval 46) | 270.93 | 0.638 | 30-DB20 | 94.25 | 0.937 | 1.05% | OK | 1.92 | -65.21% | ΔAs > 30 %
C3L | 1st-3th_long column | 450x2000 | 560 | 8 | 0.9 | 42-DB28 | 44-28 (eval 46) | 270.93 | 0.218 | 30-DB20 | 94.25 | 0.283 | 1.05% | OK | 1.88 | -65.21% | ΔAs > 30 %
C4 | B6-B1 | 450x2000 | 560 | 4.5 | 0.9 | 42-DB32 | 44-32 (eval 46) | 353.87 | 0.953 | 42-DB32 | 337.78 | 0.979 | 3.75% | OK | 1.95 | -4.547%
C4 | 4th-10th | 450x2000 | 400 | 4.5 | 0.9 | 42-DB28 | 44-28 (eval 46) | 270.93 | 0.748 | 30-DB25 | 147.26 | 0.931 | 1.64% | OK | 1.57 | -45.65% | ΔAs > 30 %
C4 | 11th-20th | 450x2000 | 400 | 4.5 | 0.9 | 22-DB25 | 22-25 | 107.99 | 0.354 | 30-DB20 | 94.25 | 0.36 | 1.05% | OK | 1.27 | -12.72%
C4L | 1st - 3th_long | 550x2000 | 560 | 7.7 | 0.9 | 42-DB32 | 44-32 | 353.87 | 0.49 | 32-DB25 | 157.08 | 0.653 | 1.43% | OK | 3 | -55.61% | ΔAs > 30 %
C5L | 1st-3th_long | 450x1000 | 560 | 8 | 0.9 | 16-DB28 | 16-28 | 98.52 | 0.369 | 16-DB20 | 50.27 | 0.553 | 1.12% | OK | 1.62 | -48.97% | ΔAs > 30 %
C5 | B6-3th | 450x1000 | 560 | 4.9 | 0.9 | 16-DB28 | 16-28 | 98.52 | 0.673 | 16-DB20 | 50.27 | 0.987 | 1.12% | OK | 2.34 | -48.97% | ΔAs > 30 %
C6 | 4th-10th | 350x2000 | 400 | 3.1 | 0.9 | 60-DB28 | 60-28 | 369.45 | 1.018 | 50-DB32 | 402.12 | 0.976 | 5.74% | OK | 1.53 | 8.843% | drawing bars D/C>1 – review
C6 | 11th-16th | 350x2000 | 400 | 3.1 | 0.9 | 22-DB28 | 20-28 | 123.15 | 0.839 | 30-DB20 | 94.25 | 0.881 | 1.35% | OK | 1.64 | -23.47%
C6 | 17th-20th | 350x2000 | 400 | 4.5 | 0.9 | 22-DB28 | — |  |  | 30-DB20 | 94.25 | 0.852 | 1.35% | OK | 1.91 |  | not on drawing
C7 | B6-1st | 450x450 | 560 | 3 | 0.9 | 8-DB28 | 8-28 | 49.26 | 0.903 | 8-DB20 | 25.13 | 0.994 | 1.24% | OK | 1 | -48.98% | ΔAs > 30 %
C9 | 16th-17th | 450x1800 | 400 | 4.5 | 0.9 | 20-DB25 | 22-25 | 107.99 | 0.583 | 28-DB20 | 87.96 | 0.616 | 1.09% | OK | 1.24 | -18.55%
C10 | 20st | 450x450 | 400 | 4.5 | 0.9 | 16-DB28 | 16-28 | 98.52 | 1.055 | 16-DB32 | 128.68 | 0.915 | 6.35% | ASK_RHO | 1.08 | 30.61% | drawing bars D/C>1 – review
C12 | 4th-10th | 300x800 | 400 | 3.5 | 0.9 | 20-DB28 | 20-28 | 123.15 | 0.813 | 14-DB28 | 86.21 | 0.977 | 3.59% | OK | 2.28 | -30%
C12 | 10th-22th | 300x800 | 400 | 3.5 | 0.9 | 12-DB25 | 12-28 | 73.89 | 0.498 | 14-DB20 | 43.98 | 0.633 | 1.83% | OK | 1.68 | -40.48% | ΔAs > 30 %
C12L | 10th-20th_long | 300x800 | 400 | 4.5 | 0.9 | 12-DB25 | 12-28 | 73.89 | 0.454 | 14-DB20 | 43.98 | 0.559 | 1.83% | OK | 1.27 | -40.48% | ΔAs > 30 %
Summary
Bands compared (with drawing bars) | 27
Drawing bars D/C > 1 by engine | 3
Engine status not OK | 1
Σ As drawing (cm², bands on drawing) | 5323.98
Σ As engine (same bands) | 4097.77
Σ ΔAs engine vs drawing | -23.03%

## Method & notes
Method
1. Inputs taken from each issued Excel calc (03_xx_..xlsx): Report (B, H, f'c, Lx, kx, βd, "Using" bars) and load sheet (P, M3, M2 per row). Each file = one mark-band; all ETABS labels in the file enveloped as one label.
2. Engine = ceda-column-design v1.2 scripts (run.py, story_ranges mode "each", fc_by_story fixed, Lu/k per file). Bands of one mark run together so the bottom-up / monotonic rule applies.
3. "D/C drawing bars" = engine 3D-surface D/C of the bars on the drawing, placed on the drawn grid (2000×450: 22 positions, 1000×450: 16, 450×450: 8, 2000×350: 20, 800×300: 12, 1200×450: 12) with symmetric tie-corner bundles. Where the count cannot be placed exactly the next symmetric count is used ("eval n").
4. Engine grid follows the v1.2 rule (c/c 125–150 → 2000 face 14 bars, 30 positions) – so bar counts differ from the drawing by design; compare As and D/C, not the count.
Assumptions / limits
A1. Lu and k as in the Excel files (Lu 4.5 m, k 0.9) except C1 B6-B5: Lu 2.75 m, k 1.0 (designer, 19 Oct 2026). Other basement bands stay 4.5 m.
A2. Shear, ties and laps not compared (load sheets carry no V).
A3. C8 (L-shape) and C11 (bent wall) not covered by the engine – skipped.
A4. C4 1st–3th "_long" Excel uses B = 55 cm while the drawing shows 450 – run as in Excel; check which is correct.
A5. C6 17th–20th, C10, C12 bands are not all shown on the drawing – compared only where shown.
A6. Rule change (designer, 19 Oct 2026): at the f'c reduction the lower story may carry less steel than the story above (C1 1st–3th 30-DB25 below 30-DB28).